## Slide 1
gp_read_value_by_label()
get_flow_units()
get_time_pacing_increment()
get_pacing_weighting()
get_sample_pacing()
bottle_and_pacing_change(pacing_input,bottle_num)
FLOW weighted sampling
TIME weighted sampling
trigger_sampler()
Flow data functions
HvF_table(stage_in)
AV_PipeFlow_cfs(vel_fps)
flow_weighted_sampling(flow)
time_weighted_sampling(pacing_input)
number_of_aliquots()
turn_on_sampling()
turn_off_sampling()
reset_sampling_params()
trigger_sampler_manually()
general functions
TASK functions
gp_write_value_by_label()

## Slide 2
Script Global variables
gp_count
time_pacing_increment
pacing_weighting
sampling_on
bottle_num
vol_in_bottle
aliquots_in_bottle
sampling_pacing
time_last_sample
sample_log
SamplePacin (either time or flow volume) – min or cf/gal
BottleNum
Incr_Flow (only used for flow-weighted sampling) – cf/gal
TimeToSampl (only used for time-weighted sampling) - min
AliquotNum - ali
Level_950 - in
Vel_950 - fps
Flow_950 – cfs/gpm
TotFlow_950 –cf/gal
Rain_950 – in
Battery_950 – V
Level_PT – in
Flow_PT (Level_PT with HvF or AV_PipeFlow_cfs) – cfs/gpm
Level_Bubbl - in
Flow_Bubble – cfs/gpm
General Purpose variables
Measurements
sampling_on
bottle_size_L
aliquot_vol_mL
bottle_num
pipe_diameter_in
flow_pacing_units
flow_pacing_data_source_units

## Slide 3
M3 = Active
M4 = Not Active
sample_weighting == ‘FLOW’
Meta Index set to flow data source
FLOW weighted sampling
pacing_weighting()
  Checks M3 and M4 to determine if flow weighting or time weighting
  ret: “TIME” or “FLOW”
At 1min interval….
get_sample_pacing()
  read current pacing and bottle_num
  compare to previous values
If pacing same then check bottle number
If pacing changed
If Bottle number same
If Bottle number changed (manually)
aliquots_in_bottle = 0
aliquots_in_bottle = 0
vol_in_bottle = 0
vol_in_bottle = 0
bottle_and_pacing_change()
flow_weighted_sampling(flow)
  flow argument from Meta Index (choose flow data source)
  Check if sampling is on (sample_on==1)
  Check if sampling is flow-weighted (get_pacing_weighting == “FLOW”)
  Get flow data source and pacing units (cfs/gpm vs cf/gal)
If sample_on=1
If pacing_weighting=“FLOW”
Then calculate incremental flow volume and add to running_total
If running_total volume >= sample_pacing then trigger sampler
trigger_sampler()
  Turn on SW12 for 0.5 sec then off
aliquots_in_bottle += 1
vol_in_bottle += ali_vol
time_last_sample
sample_log
get_sample_pacing()
Checks flow data and pacing volume units (cfs,cf/gpm,gal)
Check GP variable “sample_pacing”
Check GP variable “bottle_num”
Update values and log changes
ret: sample_pacing, bottle_num
sample_pacing = SamplePacin M1 Offset
bottle_num = BottleNum M2
bottle_num = BottleNum M2 Offset
g_running_total = g_running_total – sample_pacing
incremental_vol = flow (x60 if cfs)
g_running_total = g_running_total + incremental_vol
Subtract pacing from running_total volume, carry remainder to next measurement

## Slide 4
M3 Incr_Flow is Active
M4 is Not Active
Meta index = flow data source used to calculate incremental pacing
If using Flow_950, M3 Meta index = 8
-flow is read from the Sigma 950 flowmeter, settings must be changed in the 950
-flow units can be in gpm or cfs, flow volume will be in gal or cf accordingly
If using Flow_PT, M3 Meta index = 13
-HvF Table:
-flow can be calculated using HvF and Level_PT (M12)
-set Meta Index of M13 to 12 (Level_PT)
-use script “HvF_table”
-@MEASUREMENT HvF_table has to have the stage,flow pairs in STAGETBL
-Area Velocity:
-flow can be calculated using Vel_950 (M7) and Level_PT (M12)
-set general purpose variable “pipe_diameter_in”
-set Meta Index of M13 to 7 (Vel_950)
-use script “AV_PipeFlow_cfs” or “AV_PipeFlow_gpm”
FLOW weighted sampling
M1 SamplePacin
units = cf or gal

## Slide 5
M3 = Not Active
M4 = Active
sample_weighting == ‘TIME’
Meta Index doesn’t matter
TIME weighted sampling
pacing_weighting()
  Checks M3 and M4 to determine if flow weighting or time weighting
  ret: “TIME” or “FLOW”
At 1min interval….
time_weighted_sampling(flow)
  Check if sampling is on (sample_on==1)
  Check if sampling is time-weighted (get_pacing_weighting == “TIME”)
  Check sample_pacing (time between samples)
  Get time pacing increment (should be 1min) – set by the M4 meas interval
If sample_on=1
If pacing_weighting=“TIME”
Then subtract time_pacing_increment from running_total
If running_total volume <= 0
then trigger sampler
trigger_sampler()
  Turn on SW12 for 0.5 sec then off
aliquots_in_bottle += 1
vol_in_bottle += ali_vol
time_last_sample
sample_log
sample_pacing = SamplePacin M1 Offset
g_running_total = sample_pacing
time_pacing_increment = M4 meas interval
g_running_total = g_running_total – time_pacing_increment
Set running_total to sample_pacing for the next countdown

## Slide 6
M3 Incr_Flow is Active
M4 is Not Active
Meta index = flow data source used to calculate incremental pacing
If using Flow_950, Meta index = 8
-flow is read from the Sigma 950 flowmeter, settings must be changed in the 950
-flow units can be in gpm or cfs, flow volume will be in gal or cf accordingly
If using Flow_PT, Meta index = 13
-flow can be calculated using HvF s
-set Meta Index of M13 to 12 (Level_PT)
-use script “HvF_table”
-@MEASUREMENT HvF_table has to have the stage,flow pairs in STAGETBL
-flow can be calculated using Vel_950 and Level_PT
-set general purpose variable “pipe_diameter_in”
-set Meta Index of M13 to 7 (Vel_950)
-use script “AV_PipeFlow_cfs” or “AV_PipeFlow_gpm”
FLOW weighted sampling
M1 SamplePacin
units = cf or gal