Measurements Tab settings for Linkcomm – Sutron XLink500

| Number | Measurement Label | Device Description | Measurement Type | Configuration | Schedule | Processing | Alarms |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Measurements can be recorded on different intervals, ex flow at 5min but battery at 1hr | These settings manipulate the raw measurement | If any alarms for any measurements are triggered sampling will begin |
| M1 | SamplePacin | Sample Pacing: This is just to DISPLAY the pacing. Enter the flow or time pacing in the general purpose variables. Don't forget to change the Units to cf/gal or min | Measurement Type: Manual Entry Right digits: 0 Units: cf,gal, or min depending on program | N/A | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 00:01:00 | Enter the flow or time pacing in the general purpose variables. | Alarms (All 3): Off |
| M2 | BottleNum | Bottle Number This is just to DISPLAY the bottle number, and is manually set in the general purpose variables. BottleNum is manually updated in both flow and time weighted programs | Measurement Type: Manual Entry Right digits: 0 Units: leave blank | N/A | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 00:01:00 | Enter the bottle number in the general purpose variables. | Alarms (All 3): Off |
| M3 | Incr_Flow (only active during flow-weighted sampling) | Make this Measurement ACTIVE for Flow weighted pacing programs. And M4 not active This will show the incremental volume counting up to the pacing interval | Measurement Type: Meta Right digits: 2 or 3 Units: either cf or gal | Meta index is set to the flow data source. If flow data from the Sigma 950 should be used then Meta index = 8 (Flow_950 is M8) If Flow from PT/HvF should be used then Meta index=13 (Flow_PT is M13) | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 00:01:00 | Use script: yes Script function: flow_weighted_sampling | Alarms (All 3): Off |
| M4 | TimeToSampl (only active during time-weighted sampling) | Make this Measurement ACTIVE for Time weighted pacing programs. And M3 not active This will show the minutes counting down from the pacing to zero | Measurement Type: Meta Right digits: 0 Units: min | Meta index doesn’t matter, just set to 1 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 00:01:00 | Use script: yes Script function: time_weighted_sampling | Alarms (All 3): Off |
| M5 | AliquotNum |  | Measurement Type: Meta Right digits: 0 Units: ali | Meta index doesn’t matter, just set to 1 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 00:01:00 | Use script: yes Script function: number_of_aliquots | Alarms (All 3): Off |
| M6 | Level_950 | Sigma 950 Flowmeter - Level | Measurement Type: Modbus Right digits: 2 Units: inches | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 7 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: Whatever your interval is, typically 1min – 15min | Slope: 1 Offset: User selected (usually input in the 950 itself, not here) Use Script: no | If Sigma 950 is used for level trigger sampling start… Alarm 1: High Threshold: User selected Alarm tx mode: Tx In Only (once alarm is triggered it remains on) |
| M7 | Vel_950 | Sigma 950 Flowmeter – Velocity | Measurement Type: Modbus Right digits: 2 Units: fps | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 9 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Same as M6 | Slope: 1 Offset: 0 Use Script: no | Alarms (All 3): Off |
| M8 | Flow_950 | Sigma 950 Flowmeter – Flow | Measurement Type: Modbus Right digits: 3 Units: cfs or gpm | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 33 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Same as M6 | Slope: 1 Offset: 0 Use Script: no | Alarms (All 3): Off |
| M9 | TotFlow_950 | Sigma 950 Flowmeter – Total Flow | Measurement Type: Modbus Right digits: 3 Units: cf or gal | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 75 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Same as M6 | Slope: 1 Offset: 0 Use Script: no | Alarms (All 3): Off |
| M10 | Rain_950 | Sigma 950 Flowmeter – Rain | Measurement Type: Modbus Right digits: 2 Units: inches | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 3 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: Whatever your interval is, typically 1min – 15min | Slope: 1 Offset: 0 Use Script: No | Alarms (All 3): Off |
| M11 | Battery_950 | Sigma 950 Flowmeter – Battery | Measurement Type: Modbus Right digits: 2 Units: V | Modbus port: RS232 Modbus device id: 1 (can be 1-65,000) Modbus reg type: Holding Modbus reg number: 39 Modbus value: Float Modbus MSW: Hi Reg Modbus timeout secs: 3 Modbus retries: 3 Warmup secs: 0 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: 1hr is usually fine | Slope: 1 Offset: 0 Use Script: No | Alarms (All 3): Off You can use a “Low” alarm but it could trigger sampling |
| M12 | Level_PT | Stevens “Smart PT” Or other SDI-12 enabled PT or Bubbler (like OTT) | Measurement Type: SDI-12 Right digits: 2 Units: inches | For Stevens SmartPT SDI-12 Port: 1 SDI-12 Address: 0-9 based on number of inputs (programmed in the PT itself) SDI-12 Command: M! SDI-12 param: 1 Warmup secs: 0 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: Whatever your interval is, typically 1min – 15min | Slope: 1 Offset: User selected Use Script: no | If PT is used for level trigger sampling start… Alarm 1: High Threshold: User selected Alarm tx mode: Tx In Only (once alarm is triggered it remains on) |
| M13 | Flow_PT | Calculate Flow using HvF or AV_PipeFlow | Measurement Type: Meta Right digits: 3 Units: cfs or gpm | For HvF Meta index: 12 (reads PT level from M1) For AV_PipeFlow Meta index: # of Velocity measurement (ex 7 for Vel_950) | Same as M12 | Use script: yes For HvF, Script function: HvF_rating_table (the table also has to be programmed into the script) For AV_PipeFlow, Script function: AV_PipeFlow_gpm or AV_PipeFlow_cfs (general purpose variable “pipe_diameter_in” must also be programmed | Alarms (All 3): Off |
| M14 | Level_Bubble | OTT Bubbler | Measurement Type: SDI-12 Right digits: 2 Units: inches | For OTT CBS SDI-12 Port: 1 SDI-12 Address: 0-9 based on number of inputs (programmed in the CBS itself) SDI-12 Command: M! SDI-12 param: 3 Warmup secs: 0 | Time: 00:00:00 Averaging Time: 00:00:00 Interval: Whatever your interval is, typically 1min – 15min | Slope: 12 (to convert from ft to inches) Offset: User selected Use Script: no | If PT is used for level trigger sampling start… Alarm 1: High Threshold: User selected Alarm tx mode: Tx In Only (once alarm is triggered it remains on) |
| M15 | Flow_Bubble | Calculate Flow using HvF or AV_PipeFlow | Measurement Type: Meta Right digits: 3 Units: cfs or gpm | For HvF Meta index: 12 (reads PT level from M1) For AV_PipeFlow Meta index: # of Velocity measurement (ex 7 for Vel_950) | Same as M14 | Use script: yes For HvF, Script function: HvF_rating_table (the table also has to be programmed into the script) For AV_PipeFlow, Script function: AV_PipeFlow_gpm or AV_PipeFlow_cfs (general purpose variable “pipe_diameter_in” must also be programmed | Alarms (All 3): Off |